## Cover Sheet
|  | 客户文档编号 Customer Doc.No. |  |  |  | 文档编号 Document No.
|  | 合同编号 Contract No. |  | SCJSD20210714-407 |  | 项目号 Project No.
装置单元号 Uint.
ZHEJIANG SUPCON TECHNOLOGY CO.,LID.
项目名称 PROJECT NAME |  | 港口事业部自动化改造项目气体检测与报警系统（GDS）系统
用户名称 CUSTOMER NAME |  | 镇江海纳川物流产业发展有限责任公司
最终用户 ENDUSER NAME |  | 镇江海纳川物流产业发展有限责任公司
用户地点 LOCATION |  | 镇江
I/O AssignmenI List
3 | 2022-04-07 | 高东杰 | 储济华 |  | 毕宇 | 竣工 As_built
2 | 2021-12-16 | 高东杰 | 储济华 |  | 毕宇 | 出库 For SHIPPED
1 | 2021-07-29 | 高东杰 | 储济华 |  | 毕宇 | 批准 For Approval
版本 Rev. | 日期 Date | 制表 DRAWN | 检查 CHECKED |  | 批准 APPROVED | 版本描述 Description
For Customer's Approval
Customer Representative:
Name :
Signature :
Date :
A - Reviewed & Approved with No Comment
B - Reviewed & Approved with Comment

## IO清单
Tagname | DescripTIon | Module | Module | Type | Signal |  | Terminal | MODBUS | Eng Unit | Eu low | Eu high | Valve | Analog |  |  |  |  | Normal State |  | Power | SOE | Flash | Interface Device
|  | Place | CH.NO. |  | Source/DirecTIon | Source |  | Address |  |  |  | Action | LL | L | N | H | HH | NO/NC | 0/1 | Supply | LOGGING | Alarm | Note
NDO010101 | 备用 | R01M03L | 1 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 65 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010102 | 备用 | R01M03L | 2 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 66 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010103 | 备用 | R01M03L | 3 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 67 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010104 | 备用 | R01M03L | 4 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 68 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010105 | 备用 | R01M03L | 5 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 69 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010106 | 备用 | R01M03L | 6 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 70 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010107 | 备用 | R01M03L | 7 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 71 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010108 | 备用 | R01M03L | 8 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 72 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010109 | 备用 | R01M03L | 9 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 73 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010110 | 备用 | R01M03L | 10 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 74 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010111 | 备用 | R01M03L | 11 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 75 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010112 | 备用 | R01M03L | 12 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 76 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010113 | 备用 | R01M03L | 13 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 77 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010114 | 备用 | R01M03L | 14 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 78 | [9 empty] | NC | 1 | 220VDC | √ | √ | TU003_DOR08
NDO010115 | 备用 | R01M03L | 15 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 79 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010116 | 备用 | R01M03L | 16 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 80 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010117 | 备用 | R01M03L | 17 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 81 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010118 | 备用 | R01M03L | 18 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 82 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010119 | 备用 | R01M03L | 19 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 83 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010120 | 备用 | R01M03L | 20 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 84 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010121 | 备用 | R01M03L | 21 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 85 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010122 | 备用 | R01M03L | 22 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 86 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010123 | 备用 | R01M03L | 23 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 87 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010124 | 备用 | R01M03L | 24 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 88 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010125 | 备用 | R01M03L | 25 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 89 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010126 | 备用 | R01M03L | 26 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 90 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010127 | 备用 | R01M03L | 27 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 91 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010128 | 备用 | R01M03L | 28 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 92 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
NDO010129 | 备用 | R01M03L | 29 | DO1 | 继电器端子板→安全继电器→端子→电磁阀 | 有源 | NO | 93 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
AL-90000 | 控制室声光报警仪 | R01M03L | 30 | DO1 | 继电器端子板→安全继电器→端子→报警仪 | 有源 | NO | 94 | [9 empty] | NC | 1 | 24VDC | √ | √ | TU003_DOR08
BUZZER | 蜂鸣器 | R01M03L | 31 | DO1 | 继电器端子板→安全继电器→端子→辅操台 | 有源 | NO | 95 | [9 empty] | NO | 1 | 24VDC |  | √ | TU003_DOR08
ALM_LAMP | 综合报警灯 | R01M03L | 32 | DO1 | 继电器端子板→安全继电器→端子→辅操台 | 有源 | NO | 96 | [9 empty] | NO | 1 | 24VDC |  | √ | TU003_DOR08
aCA02_5014 | 万吨贮槽V5304西乙醇可燃气体检测 | R01M04L | 1 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7873 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5015 | 万吨贮槽V5301西甲醇可燃气体检测 | R01M04L | 2 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7875 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5016 | 万吨贮槽V5303西甲醇可燃气体检测 | R01M04L | 3 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7877 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5017 | 万吨贮槽V5302西乙醇可燃气体检测 | R01M04L | 4 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7879 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5108 | 万吨贮槽V5306西醋酸可燃气体检测 | R01M04L | 5 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7881 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5109 | 万吨贮槽V5305西醋酸可燃气体检测 | R01M04L | 6 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7883 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5807 | 万吨贮槽V5306东醋酸可燃气体检测 | R01M04L | 7 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7885 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5110 | 万吨贮槽V5305防火梯外西醋酸可燃气体检测 | R01M04L | 8 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7887 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5809 | 万吨贮槽V5305东醋酸可燃气体检测 | R01M04L | 9 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7889 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5810 | 万吨贮槽V5302东乙醇可燃气体检测 | R01M04L | 10 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7891 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5811 | 万吨贮槽V5301东甲醇可燃气体检测 | R01M04L | 11 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7893 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5813 | 万吨贮槽V5304东乙醇可燃气体检测 | R01M04L | 12 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7895 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5814 | 万吨贮槽V5303东甲醇可燃气体检测 | R01M04L | 13 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7897 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5837 | 万方甲醇泵区可燃气体检测 | R01M04L | 14 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7899 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5781 | 收发P5308C乙醇发车泵可燃气体检测 | R01M04L | 15 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7901 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5782 | 收发P5302B甲醇输送泵可燃气体检测 | R01M04L | 16 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7903 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5783 | 收发P5304C乙醇收发泵可燃气体检测 | R01M04L | 17 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7905 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5862 | 万方污水泵区可燃气体检测 | R01M04L | 18 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7907 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5840 | 万方甲醇V5301西北可燃气体检测 | R01M04L | 19 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7909 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5841 | 万方甲醇V5301西南可燃气体检测 | R01M04L | 20 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7911 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5842 | 万方乙醇V5302西北可燃气体检测 | R01M04L | 21 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7913 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5843 | 万方甲醇V5303西北可燃气体检测 | R01M04L | 22 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7915 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5844 | 万方乙醇V5304西北可燃气体检测 | R01M04L | 23 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7917 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5845 | 万方乙醇V5304东南可燃气体检测 | R01M04L | 24 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7919 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5846 | 万方醋酸V5305西北可燃气体检测 | R01M04L | 25 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7921 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5847 | 万方醋酸V5305西南可燃气体检测 | R01M04L | 26 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7923 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5848 | 万方醋酸V5306西南可燃气体检测 | R01M04L | 27 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7925 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5301 | 万吨贮槽V5303西可燃气体检测 | R01M04L | 28 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7927 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5302 | 万吨贮槽V5301南可燃气体检测 | R01M04L | 29 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7929 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5303 | 万吨贮槽V5301东可燃气体检测 | R01M04L | 30 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 | 7931 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
NAI010335 | 备用 | R01M04L | 31 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010336 | 备用 | R01M04L | 32 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
aCA02_5003 | 收发贮槽V5201南醋酸可燃气体检测 | R01M05L | 1 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7937 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5004 | 收发贮槽V35101北乙酯可燃气体检测 | R01M05L | 2 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7939 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5772 | 收发贮槽V35100北乙酯可燃气体检测 | R01M05L | 3 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7941 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5773 | 收发贮槽V35101南乙酯可燃气体检测 | R01M05L | 4 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7943 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5776 | 收发P5208A醋酸可燃气体检测 | R01M05L | 5 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7945 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5777 | 收发P35102泵乙酯可燃气体检测 | R01M05L | 6 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7947 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5802 | 收发气体小屋可燃气体检测 | R01M05L | 7 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7949 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5805 | 收发贮槽V35102南乙酯可燃气体检测 | R01M05L | 8 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7951 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5808 | 收发贮槽V35103南乙酯可燃气体检测 | R01M05L | 9 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7953 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5812 | 收发贮槽V35102北乙酯可燃气体检测 | R01M05L | 10 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7955 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5815 | 收发贮槽V35100南乙酯可燃气体检测 | R01M05L | 11 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7957 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5823 | 收发乙酯VOC机柜南可燃气体检测 | R01M05L | 12 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7959 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5828 | 收发P5312C可燃气体检测 | R01M05L | 13 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7961 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5829 | 收发P5310A可燃气体检测 | R01M05L | 14 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7963 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5830 | 千方V5201西可燃气体检测 | R01M05L | 15 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7965 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5831 | 千方V5206西可燃气体检测 | R01M05L | 16 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7967 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5832 | 千方V5206东可燃气体检测 | R01M05L | 17 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7969 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5833 | 千方精制酸泵区可燃气体检测 | R01M05L | 18 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7971 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5834 | V35103东北可燃气体检测 | R01M05L | 19 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7973 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5835 | 乙酯收集罐V001处可燃气体检测 | R01M05L | 20 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7975 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5849 | 千方醋酸V5201北可燃气体检测 | R01M05L | 21 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7977 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5850 | 千方醋酸V5206北可燃气体检测 | R01M05L | 22 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7979 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5851 | 千方乙酯V35100西北可燃气体检测 | R01M05L | 23 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7981 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5852 | 千方乙酯V35101西北可燃气体检测 | R01M05L | 24 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7983 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5853 | 千方乙酯V35102西北可燃气体检测 | R01M05L | 25 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7985 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5854 | 千方乙酯V35103西北可燃气体检测 | R01M05L | 26 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7987 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
NAI010363 | 备用 | R01M05L | 27 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7989 | % | 0 | 100 |  |  |  |  | 35 | 60 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5801 | 收发气体小屋氧气检测 | R01M05L | 28 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7991 | % | 0 | 100 |  |  | 19.5 |  | 23.5 |  |  |  | 24VDC |  | √ | 三线制端子
aCA02_5838 | CO2球罐A下侧氧气检测 | R01M05L | 29 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7993 | % | 0 | 100 |  |  | 19.5 |  | 23.5 |  |  |  | 24VDC |  | √ | 三线制端子
aCA02_5839 | CO2球罐B下侧氧气检测 | R01M05L | 30 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 | 7995 | % | 0 | 100 |  |  | 19.5 |  | 23.5 |  |  |  | 24VDC |  | √ | 三线制端子
NAI010367 | 备用 | R01M05L | 31 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010368 | 备用 | R01M05L | 32 | AI1 | 端子板←端子←变送器 | 4-20mA | TBC302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
aCA02_5821 | 收发发车岛北(醋酸2)可燃气体检测 | R01M06L | 1 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8001 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5822 | 收发发车岛南(乙酯3)可燃气体检测 | R01M06L | 2 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8003 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5824 | 收发收车装置9/10收车台可燃气体检测 | R01M06L | 3 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8005 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5825 | 收发收车装置7/8收车台可燃气体检测 | R01M06L | 4 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8007 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5826 | 收发收车装置13/14收车台可燃气体检测 | R01M06L | 5 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8009 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5827 | 收发收车装置11/12收车台可燃气体检测 | R01M06L | 6 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8011 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5836 | 甲醇收车岛7号口处可燃气体检测 | R01M06L | 7 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8013 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5855 | 收车岛9# 10#甲醇二楼可燃气体检测 | R01M06L | 8 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8015 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5856 | 收车岛7# 8#甲醇二楼可燃气体检测 | R01M06L | 9 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8017 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5857 | 发车岛5# 6#甲醇二楼可燃气体检测 | R01M06L | 10 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8019 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5858 | 发车岛3# 4#乙酯一楼可燃气体检测 | R01M06L | 11 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8021 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5859 | 发车岛3# 4#乙酯二楼可燃气体检测 | R01M06L | 12 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8023 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5860 | 收车岛11# 12#乙醇二楼可燃气体检测 | R01M06L | 13 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8025 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5861 | 收车岛13# 14#乙醇二楼可燃气体检测 | R01M06L | 14 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8027 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5790 | 收发1#泊位门口甲醇可燃气体检测 | R01M06L | 15 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8029 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5791 | 收发1#泊位甲醇流量计旁可燃气体检测 | R01M06L | 16 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8031 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5795 | 收发2#泊位发放处东醋酸可燃气体检测 | R01M06L | 17 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8033 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5796 | 收发2#泊位门口醋酸可燃气体检测 | R01M06L | 18 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8035 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5792 | 收发1#泊位发放处东可燃气体浓度 | R01M06L | 19 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8037 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5793 | 收发2#泊位发放处西醋酸可燃气体检测 | R01M06L | 20 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8039 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
aCA02_5794 | 收发2#泊位发放处中可燃气体浓度 | R01M06L | 21 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 | 8041 | % | 0 | 100 |  |  |  |  | 25 | 50 |  |  | 24VDC |  | √ | 三线制端子
NAI010390 | 备用 | R01M06L | 22 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010391 | 备用 | R01M06L | 23 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010392 | 备用 | R01M06L | 24 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010393 | 备用 | R01M06L | 25 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010394 | 备用 | R01M06L | 26 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010395 | 备用 | R01M06L | 27 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010396 | 备用 | R01M06L | 28 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010397 | 备用 | R01M06L | 29 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010398 | 备用 | R01M06L | 30 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010399 | 备用 | R01M06L | 31 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010400 | 备用 | R01M06L | 32 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD301 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010401 | 备用 | R01M07L | 1 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010402 | 备用 | R01M07L | 2 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010403 | 备用 | R01M07L | 3 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010404 | 备用 | R01M07L | 4 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010405 | 备用 | R01M07L | 5 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 25 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010406 | 备用 | R01M07L | 6 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010407 | 备用 | R01M07L | 7 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010408 | 备用 | R01M07L | 8 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010409 | 备用 | R01M07L | 9 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010410 | 备用 | R01M07L | 10 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010411 | 备用 | R01M07L | 11 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010412 | 备用 | R01M07L | 12 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010413 | 备用 | R01M07L | 13 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010414 | 备用 | R01M07L | 14 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010415 | 备用 | R01M07L | 15 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010416 | 备用 | R01M07L | 16 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010417 | 备用 | R01M07L | 17 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010418 | 备用 | R01M07L | 18 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010419 | 备用 | R01M07L | 19 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010420 | 备用 | R01M07L | 20 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010421 | 备用 | R01M07L | 21 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010422 | 备用 | R01M07L | 22 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010423 | 备用 | R01M07L | 23 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010424 | 备用 | R01M07L | 24 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010425 | 备用 | R01M07L | 25 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010426 | 备用 | R01M07L | 26 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010427 | 备用 | R01M07L | 27 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010428 | 备用 | R01M07L | 28 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010429 | 备用 | R01M07L | 29 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010430 | 备用 | R01M07L | 30 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010431 | 备用 | R01M07L | 31 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010432 | 备用 | R01M07L | 32 | AI1 | 端子板←端子←变送器 | 4-20mA | TBD302 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010433 | 备用 | R01M08L | 1 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010434 | 备用 | R01M08L | 2 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010435 | 备用 | R01M08L | 3 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010436 | 备用 | R01M08L | 4 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010437 | 备用 | R01M08L | 5 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010438 | 备用 | R01M08L | 6 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010439 | 备用 | R01M08L | 7 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010440 | 备用 | R01M08L | 8 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010441 | 备用 | R01M08L | 9 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010442 | 备用 | R01M08L | 10 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010443 | 备用 | R01M08L | 11 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010444 | 备用 | R01M08L | 12 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010445 | 备用 | R01M08L | 13 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010446 | 备用 | R01M08L | 14 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010447 | 备用 | R01M08L | 15 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010448 | 备用 | R01M08L | 16 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010449 | 备用 | R01M08L | 17 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010450 | 备用 | R01M08L | 18 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010451 | 备用 | R01M08L | 19 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010452 | 备用 | R01M08L | 20 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010453 | 备用 | R01M08L | 21 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010454 | 备用 | R01M08L | 22 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010455 | 备用 | R01M08L | 23 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010456 | 备用 | R01M08L | 24 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010457 | 备用 | R01M08L | 25 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010458 | 备用 | R01M08L | 26 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010459 | 备用 | R01M08L | 27 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010460 | 备用 | R01M08L | 28 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010461 | 备用 | R01M08L | 29 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010462 | 备用 | R01M08L | 30 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010463 | 备用 | R01M08L | 31 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子
NAI010464 | 备用 | R01M08L | 32 | AI1 | 备用 | 4-20mA | 备用 |  | % | 0 | 100 | [8 empty] | 24VDC |  | √ | 三线制端子